## Slide 1: CrossMEP: A Tiered Synthetic Dataset of Multi-Trade MEP Cross-Sections
A support-design problem distribution for learning-based structural support assembly synthesis
Lavinia Pedrollo ¹ · David Gvadzabia ² · Torben Graeber ³ · Martin Fischer ¹
¹ Stanford University, CIFE ² Lafayette College ³ Hilti AG
43rd International CIB W78 Conference · IT in Construction · New Delhi, 6–8 October 2026
Notes: Hi, I'm Lavinia, a PhD student at Stanford University, and today I am happy to present CrossMEP, which is the dataset we built when we found that the data to learn support design from did not exist. Support design is the one part of MEP that every tool coordinates, every tool checks, and no tool does. A hospital has ten thousand of these supports, each chosen by hand from a catalog. We think a machine can learn to choose them, and what has stopped anyone trying is not the algorithm. It is that nobody had the problems to practise on. So we built the problems. (0:00)

## Slide 2: The synthesis of structural support assemblies (SSAs) takes 25% of MEP design effort because every assembly must be designed individually
1 unit = 1 structural support assembly (SSA)
200,000 sq ft hospital · every red mark is one support
≈ 10,000
support assemblies in one hospital project, each one its own design
×
20 min – 2 h
of engineering time for each assembly, designed one by one
=
≈ 25 %
of MEP design effort, about $600k of engineering cost per project
Approximate practitioner estimates [1]. [1] Pedrollo, Graeber & Fischer (2026), Feasibility-aware sequential synthesis of structural support assemblies, ISARC 2026
Notes: Here is the scale. This is a hospital, and every red mark is a place where services hang from the structure. A modular support groups several services on one prefabricated frame: a structural support assembly. A hospital this size needs about ten thousand of them, each designed individually, twenty minutes to two hours apiece. Add it up and it is about a quarter of the MEP design effort. Practitioner estimates, but these are the numbers people live with. (0:45)

## Slide 3: An SSA designer turns one MEP cross-section into a feasible structural support assembly
CONTEXT · the brief
Concrete slab, 200 mm
Duct 600 × 400
DN80, insulated
DN40
Cable tray 300
Every element with its kind, trade, size, insulation, position and load per metre. Nothing else.
SSA designer
from a catalog
FEASIBLE SSA · the answer
Concrete slab, 200 mm
anchor
threaded rod
pipe clamps
channel
Rod trapeze
✓ statics
✓ anchors
✓ connectors
✓ buildable
The synthesis problem as defined at ISARC 2026 [1]. [1] Pedrollo, Graeber & Fischer (2026), Feasibility-aware sequential synthesis of structural support assemblies, ISARC 2026
Notes: So what exactly is designed, and from what? In: one cross-section at a hanger. The structure it hangs from, and the services crossing it, each with its trade, position, size and weight per metre. We call that the context. It is the brief. Out: assemblies of catalog parts that carry those services to the structure, checked for statics, anchors, connectors and buildability, ranked by cost. That is the answer. Hold on to these two words, because CrossMEP is contexts only. It contains no assemblies. (1:15)

## Slide 4: Existing tools coordinate and verify modular support assemblies, but their synthesis remains manual because it relies on tacit engineering expertise and complex catalog-driven rules
Coordinate the model
tools
services routed and clash-free
Synthesize the assembly
by hand
topology and parts chosen by an engineer [1]
?
Verify the design
tools
statics, anchors and connectors checked
✓ statics
✓ anchors
✓ connectors
Why the middle step resists automation
Tacit judgment
the topology comes from experience
Rule explosion
constraints interact across thousands of combinations
Catalog volatility
catalogs change faster than rule systems
[1] Pedrollo, Graeber & Fischer (2026), Feasibility-aware sequential synthesis of structural support assemblies, ISARC 2026 [2] Pedrollo, Gvadzabia, Graeber & Fischer (2026), CrossMEP, CIB W78 2026 (this paper) [3] Korman, Fischer & Tatum (2003), Knowledge and reasoning for MEP coordination, J. Constr. Eng. Manage. 129(6)
Notes: Why is this still done by hand? A designer works from one section at each hanger, after coordination. Tools coordinate the model and check a design, but they do not choose the layout or the parts. Three reasons it has resisted automation: the topology comes from experience, the rules interact across thousands of combinations, and catalogs change faster than rule systems can be rewritten. (1:50)

## Slide 5: A learning method needs thousands of contexts to practise on, and real projects give too few, so we generate them
How a learning method learns, round after round
Context
one section at a hanger, without the answer
Learning method
a black box that proposes a design
Proposed design
an assembly: channel, rods, clamps, anchors
Check
statics, anchors, connectors, buildability, cost
1
2
3
4
pass or fail is fed back, and the method improves
Real projects
too few, not diverse enough
A handful of sections, from one project with one trade mix, and confidential. Not enough to practise on, and a method tuned on them only fits that project.
CrossMEP generates them
unlimited, diverse
As many contexts as a method needs: every tier from one to eight elements, kinds and surfaces varied, a new seed a new set. And one fixed benchmark, never trained on, to judge every method on.
Notes: So how would a machine learn it? Give it a context. Let it propose an assembly. Check the assembly, and feed pass or fail back. Round after round, it gets better. But every round needs a new context, and that is where it stops. Real projects give a handful of sections, all from the same kind of job and confidential: too few to practise on, and a method tuned on them only fits that job. So we generate the contexts, as many as a method needs, and we fix one benchmark to judge every method on. (2:15)

## Slide 6: The ninety real designs we had came from one project and filled one corner of the design space, so CrossMEP covers all of it by construction
The real designs we had ninety · one project · confidential
elements at the hanger: 1 … 8
kinds, trades, surface
ducts and many pipes, no trays, nothing as simple as one pipe
a method tuned here only fits that project
CrossMEP every tier · kinds and surfaces varied · unlimited
elements at the hanger: 1 … 8
kinds, trades, surface
CrossMEP at a glance
7,000
contexts in four splits, on disjoint seeds
31,484
elements: pipes, trays, ducts, conduits; six trades
C1–C8
eight tiers by exact element count
0 labels
the brief, not the answer
Traced
every constant sourced or declared
Open
data CC BY 4.0, code MIT, seeded generator
Notes: How scarce? The real designs we could get were ninety, from one project. Nearly every one had a duct and many pipes. Not one had a cable tray, and not one was as simple as a single pipe: one corner of the design space. A method tuned on them measures fit to that project. So CrossMEP fills the space by construction: every tier from one element to eight, kinds and surfaces varied, without limit. A new seed is a new set. Seven thousand contexts are the release, not the ceiling. (2:55)

## Slide 7: One context is exactly what a support designer receives at one hanger, without the answer
● ventilation ● electrical ● heating
What every element carries
kind
service, trade
size
insulation
position
load = kN/m × span
What the support designer is given
Element | Trade | Ins. mm | kN/m | Span | kN at support
400×250 duct | ● ventilation | 0 | 0.115 | 2.4 m | 0.28
400×250 duct | ● ventilation | 0 | 0.115 | 2.4 m | 0.28
450 tray | ● electrical | 0 | 0.809 | 2.0 m | 1.62
300 tray | ● electrical | 0 | 0.540 | 2.0 m | 1.08
DN20 | ● heating | 20 | 0.019 | 2.1 m | 0.04
200 mm
ceiling slab, concrete C30
3.30 kN
total load at this support
44 mm
closest clear gap, 2 rows
Not given, by design: channel, rods, clamps, anchors. No correct answer either: a feasible support depends on the catalog you build from.
Notes: Here is one context: a two-dimensional section at one support. Each element has its kind, service and trade, its size, insulation and position, and its load: weight per metre times the span it was sized at. Add the surface, slab or wall, and that is all. No channel, no rods, no anchors, no correct answer, because a feasible support depends on the catalog you build from. (3:35)

## Slide 8: Every section is built the way trades run services, with gaps measured on a real building
1
Tier
Cn fixes the exact element count, n = 1 … 8
2
Surface
ceiling or wall (78 / 22 %); concrete, 150–300 mm thick
3
Services
grouped as trades run [3]: hot + cold, flow + return, conduit groups, 1–2 trays, ducts
4
Rows
bulky first: ducts nearest the slab, then trays and conduits, then pipes
5
Spacing
gaps drawn from a built project [12], at least 25 mm; electrical above wet on walls [10]
6
Check
every pair 25 mm clear, rows centred, everything recorded; same seed, same file
● ventilation ● electrical ● heating
One generated context, tier C8: 8 services on 3 rows, ducts nearest the slab, then the tray and conduits, then the pipe. The gap marked on the sheet is one draw from the measured distribution; the same seed gives the same section.
[3] Korman, Fischer & Tatum (2003), Knowledge and reasoning for MEP coordination, J. Constr. Eng. Manage. 129(6) [10] IET On-Site Guide (BS 7671), conduit support spacing; BS 7671 Reg. 528.3.2 [12] buildingSMART International (2020), Duplex Apartment and Medical-Dental Clinic sample IFC files, CC BY 4.0
Notes: How is a context made? By rules an engineer would recognize. The tier fixes the element count. We pick the surface and fill it the way trades run services: hot and cold together, flow and return together, conduits in groups, bulky services nearest the slab. Gaps are drawn from gaps measured on a built project, never below twenty-five millimetres. On walls, electrical stays above water. Same seed, same file. (4:00)

## Slide 9: Every number is traced to a standard, to a measurement, or to a choice we declare as ours
Pipes DN15–150
Sizes EN 10220 / EN 10255 medium series [4]
Load steel + water × ASME B31.1 water-service span [8]
Insulation
Sizes GEG Anlage 8, heated lines [11]; 30 / 50 mm condensation control, chilled
Load adds to the size, not the load
Cable trays 150–600
Sizes IEC 61537 systems [6] in NEMA VE 1 widths [7]
Load 50 kg/m full at 300 mm × 2.0 m, below the shortest NEMA class span [7]
Ducts
Sizes EN 1505 rectangular, EN 1506 round [5]
Load manufacturer weight table with flanges × 2.4 m (SMACNA) [9]
Conduits Ø20–50
Sizes IEC 61386-1 [6], parallel groups of 2–6
Load steel tube + 40 % cable fill × 2.0 m (IET / BS 7671) [10]
Standards
what each element is and weighs: sizes, walls, spans, insulation [4]–[11]
Measured
how close neighbours sit: clear gaps and row stagger from two open buildings [12]
Declared
our choices, labelled as such: trade mix, ceiling / wall 78 / 22 %, number of rows
Every constant carries its source and its status, and why each standard was chosen over its alternatives is written down with it.
[4] EN 10220:2002, EN 10255:2004 (steel tubes: dimensions, medium series) [5] EN 1505:1997, EN 1506:2007 (sheet-metal air ducts: rectangular and circular dimensions) [6] IEC 61386-1 (conduit systems), IEC 61537 (cable tray and ladder systems) [7] NEMA VE 1 (metal cable tray systems: widths, load-class spans) [8] ASME B31.1 Table 121.5 (hanger spacing), as republished in the ASHRAE Handbook, HVAC Systems and Equipment [9] SMACNA, HVAC Duct Construction Standards, Metal and Flexible, Table 5-1 [10] IET On-Site Guide (BS 7671), conduit support spacing; BS 7671 Reg. 528.3.2 [11] GEG (Gebäudeenergiegesetz), Anlage 8 (pipe insulation thickness) [12] buildingSMART International (2020), Duplex Apartment and Medical-Dental Clinic sample IFC files, CC BY 4.0
Notes: Where do the numbers come from? Sizes, weights and spans from standards: EN for pipes and ducts, IEC for conduits and trays, ASME for spans, GEG for insulation. Spacing from measured open buildings. And a few choices of our own, like the trade mix, labelled as choices. (4:30)

## Slide 10: The tier fixes the element count, and load and congestion grow with it as the rules intend
Chart: Heavier with the tier: median load at the support (kN)
| C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8
benchmark median | 0.3 | 0.24 | 1.04 | 0.94 | 1.22 | 1.36 | 2.24 | 2.04
population median (2,000 per tier) | 0.21 | 0.4 | 0.8 | 1.06 | 1.485 | 1.875 | 2.04 | 2.47
Chart: Tighter with the tier: median closest clear gap (mm)
| C2 | C3 | C4 | C5 | C6 | C7 | C8
benchmark median | 130.3 | 88.75 | 76.8 | 71.6 | 68.6 | 60.6 | 51.2
population median (2,000 per tier) | 149 | 99.45 | 82.125 | 69.8 | 66.6 | 59.95 | 54.95
A check that the dataset behaves as designed, not a discovery: the tier fixes the element count; load and congestion follow from the rules. Within a tier, kinds, trades, surfaces and stacking all vary. Load rises with the tier (rank correlation +0.46 on the benchmark, 125 contexts per tier; the population medians rise at every step) and the closest gap narrows at every step (−0.38); intervals are bootstrapped over contexts.
Notes: Three analyses. The first is a design check. Each tier adds one element: C1 is a single service, the most common support in any building; C8 has eight. Within a tier everything else varies, so the element count is the one controlled axis. Load at the support rises with the tier, from about 0.3 to 2.0 kilonewtons, and the closest gap narrows at every step, from 130 to about 51 millimetres. The dataset behaves as designed. (4:50)

## Slide 11: Generated spacing matches a clinic the generator never saw to within 32 millimetres
Chart: A building the generator never saw
| 0 | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575
measured: Medical-Dental Clinic, 797 pipe pairs | 1.4871 | 6.1831 | 2.4785 | 8.1137 | 13.3838 | 7.6963 | 5.4526 | 7.3572 | 8.1398 | 6.444 | 4.5395 | 3.3655 | 5.557 | 6.4701 | 2.4785 | 0.39134 | 2.2959 | 1.461 | 0.62614 | 1.1479 | 1.3306 | 2.2176 | 1.1218 | 0.26089
generated: CrossMEP benchmark, 1,690 pipe pairs | 0 | 0.76923 | 3.1953 | 6.2722 | 7.574 | 9.2899 | 9.1124 | 8.6982 | 7.929 | 6.7456 | 6.213 | 5.7396 | 4.9112 | 3.2544 | 2.9586 | 2.1302 | 2.4852 | 1.716 | 1.8935 | 1.1243 | 2.1302 | 2.9586 | 1.7751 | 1.1243
How far apart the distributions are: Wasserstein-1 (mm) with 95 % interval
0
40
80
120
160
generated ↔ Clinic
32
Duplex MEP ↔ Duplex Plumbing
26
generated ↔ Duplex MEP
76
Clinic ↔ Duplex MEP
71
generated ↔ Duplex Plumbing
88
Clinic ↔ Duplex Plumbing
85
● generated vs a real model ● real vs real | noise floor: what a perfect generator would show
32 mm
generator to clinic (95 % CI 17–48); fitted on the duplex, clinic held out
26 mm
the duplex's own two models from each other: about as close as real is to real
190 mm
what a fixed 25 mm gap would be from the clinic
Sections every 250 mm, clinic pipe pairs weighted by shared length; models: buildingSMART Duplex Apartment and Medical-Dental Clinic [12]. [12] buildingSMART International (2020), Duplex Apartment and Medical-Dental Clinic sample IFC files, CC BY 4.0
Notes: The second is the one the generator could fail: is the spacing realistic in a building it has never seen? The gap distribution was fitted on a residential duplex. We held out a medical clinic, cut it into sections every 250 millimetres, and measured the gaps between pipes side by side. Generator to clinic: 32 millimetres. Above the 8 a perfect generator would show, but about as close as the duplex's own two models are to each other. A fixed 25-millimetre gap would be about 190 off. (5:20)

## Slide 12: The paper’s two clamp sizes reach one pipe in seven, and the dataset says which sizes to add
Chart: Pipes by nominal size: what the two-size catalog attaches
| DN15 | DN20 | DN25 | DN32 | DN40 | DN50 | DN65 | DN80 | DN100 | DN125 | DN150
attachable | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0
no size fits | 137 | 239 | 390 | 335 | 0 | 316 | 190 | 160 | 188 | 85 | 88
Chart: Best share of pipes (%) that any k clamp sizes could attach
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
best possible share (%) | 22.9502 | 38.0627 | 50.6431 | 60.4904 | 68.7299 | 76.2058 | 81.3907 | 85.209 | 87.7814 | 90.2331 | 92.6045 | 94.8553 | 96.9051 | 98.955 | 100
14.5 %
of benchmark pipes attachable with the paper’s two sizes [2] (95 % CI 12.7–16.2); every one is DN40
38.1 %
with two sizes placed where the pipes are; 76 % with six, and every pipe with 15
0 of 2,012
trays, ducts and conduits: a pipe-clamp catalog defines no attachment. Load never binds (1.97 vs 2.5 kN)
[2] Pedrollo, Gvadzabia, Graeber & Fischer (2026), CrossMEP, CIB W78 2026 (this paper)
Notes: The third is a use of the dataset: what must a catalog of clamps cover? Our paper's two-size catalog attaches 14.5 percent of the pipes, interval 13 to 16, all one size, DN40. Trays, ducts and conduits are not covered at all. On the right, what the dataset asks of any catalog: two well-placed sizes reach 38 percent, six sizes 76, fifteen every pipe. What the catalog should contain becomes a measurement. (5:55)

## Slide 13: Pick a tier or an exact mix and a seed, and the Generator Studio returns the designer’s brief
In: the parameters
Out: section A–A as the designer receives it, and what it carries
Out: the same run in 3D, cut at the section
Scan to open the studio
every section is a stored output of the released generator, with the call that reproduces it
Notes: Let me show it. This is the Generator Studio. I choose what crosses the hanger, a tier or an exact mix, and a seed. Out comes the section a designer receives, drawn as an engineer would issue it: every service at true size, its level, its load, the closest gap, and the run in 3D. Every section is a stored output of the released generator. Scan the code to try it. [Live: switch to the studio, click C3, then Generate another twice, then Exact mix with a duct. If the demo fails, stay on this slide: its screenshot is the fallback. Before the talk: open the studio once with internet, set its link sharing to public, scan the QR from a phone not logged in.] (6:25)

## Slide 14: Methods train on the generator and are compared on one fixed benchmark, tier by tier
Generator
unlimited problems: a new seed is a new set; a curriculum from C1 up to C8
train on
Train
5,000 contexts (seed 1000); validation 500, test 500, on their own seeds
evaluate on
Benchmark
1,000 contexts, 125 per tier, seed 42: never trained on, the same for every method
then
Report
per tier, with 95 % intervals and paired tests between methods
import crossmep.tasks as cm
data = cm.load("benchmark") # 1,000 contexts, or generate your own mix
from crossmep.evaluate import score, compare
score(my_results, data) # per tier, 95 % CI compare(mine, baseline, data) # paired test
Four lines to load, score and compare; loading, metrics and scoring need only the Python standard library, the generator needs NumPy. The same files serve reinforcement learning, constraint programming and benchmarking: there are no labels to fit a method to.
Notes: Using it takes a few lines: load a split, filter by composition, or generate your own mix. Four splits on disjoint seeds: five thousand to train, five hundred each for validation and test, and a benchmark of a thousand, a hundred and twenty-five per tier. The same files serve reinforcement learning, constraint programming and benchmarking, and we ship the scoring. Train on the generator. Evaluate on the benchmark, the same contexts for every method. Report per tier, with intervals and paired tests. (7:30)

## Slide 15: Today CrossMEP is one section at one support, and next come a checker and real projects
Scope
One cross-section at one support: routing, branches and support spacing are outside it; the span is recorded, so a method can vary it
Realism checked on two open buildings, a residential duplex and a medical clinic; congested racks rest on practice and standards
Trade mix and tier composition are design choices, not survey results
Synthetic: not for the structural design of real installations
Next
1
A public checker for support designs, with best-known costs from an exact solver on the small tiers
2
The catalog as an input: generated catalogs, and catalogs a method has never seen
3
A real test set: sections from commercial projects with supports designed by engineers
If you coordinate services or design supports, open the studio, generate the sections you know from your projects, and tell us what looks wrong. Every rule is one documented constant away from being changed.
Notes: Scope. CrossMEP is one section at one support. Pipe spacing was checked on two open buildings; the rest rests on practice and standards, and the trade mix is a design choice. It is not for the structural design of real installations. Next: a public checker, so methods can be compared on the answer; the catalog as an input; and a real test set from commercial projects, with supports designed by engineers. That is where I would value your eye. (8:05)

## Slide 16: Support design finally has open problems to learn from
CrossMEP is the brief, not the answer: seven thousand support-design problems, open to anyone who wants to teach a machine to design supports.
Data CC BY 4.0, code MIT. Not for the structural design of real installations.
7,000
support-design problems in eight tiers
Sourced
every constant sourced or declared
Checked
pipe gaps tested on two open buildings
Open
data, code and generator
github.com/lavinia-ped/CrossMEP_Dataset
laviniap@stanford.edu
Notes: To sum up: CrossMEP is the brief, not the answer. Seven thousand support-design problems, every constant sourced or declared, spacing checked on two open buildings, all of it open. If you coordinate services or design supports, try the studio and tell me what looks wrong. Thank you. (8:35)